## SS Emissions
Attachment A
Table A-1
Seneca Sustainable Energy, LLC - 206470
Estimated Daily Metals Emissions During Startup of EU-1: Wood-Fired Cogeneration Power Plant
Boiler Max S/S Heat Input Rate = | 84.8463 | MMBtu/hr | (Heat input rate at which ESP is online - See Plant Operating Data Table A-2)
Boiler Max S/S Hours = | 12 | Hours | (Number of hrs operating w/o ESP online - Assumed max. - Typical is ~ 6 hrs)
Boiler Max S/S Day Heat Input Rate = | 352.8 | MMBtu/hr | (Max heat input rate reached 24 hours from startup - Boiler rated capacity)
Cumulative Heat Input pre-ESP = | 509.0775 | MMBtu | (Cumulative heat input without ESP online)
Cumulative Heat Input post-ESP = | 2625.8775 | MMBtu | (Cumulative heat input after ESP online)
Metal TAC | CAS # | Steady State Emission Factor (lb/MMBtu) | Reference | Startup Emission Factor (lb/MMBtu) | Reference | Max. Daily Emissions (lb/day)
Antimony | 7440-36-0 | 3.02e-07 | (1) | 3.11e-06 | (2) | 0.0023762
Arsenic | 7440-38-2 | 1.88e-06 | (1) | 7.2e-06 | (2) | 0.008602
Barium and Compounds | 7440-39-3 | 0.00021 | (1) | 0.00483 | (2) | 3.0103
Beryllium | 7440-41-7 | 3.01e-08 | (1) | 1.34e-07 | (2) | 0.00014726
Cadmium Compounds | 7440-43-9 | 3.66e-07 | (1) | 4.99e-06 | (2) | 0.0035014
Chromium (VI) | 18540-29-9 | 2.72e-07 | (1) | 6.97e-06 | (2) | 0.0042625
Cobalt Compounds | 7440-48-4 | 2.35e-06 | (1) | 1.67e-06 | (2) | 0.007021
Copper Compounds | 7440-50-8 | 4.99e-06 | (1) | 0.000111 | (2) | 0.069611
Lead | 7439-92-1 | 5.21e-06 | (1) | 3.11e-05 | (2) | 0.029513
Manganese Compounds | 7439-96-5 | 9.13e-05 | (1) | 0.00276 | (2) | 1.6448
Mercury | 7439-97-6 | 1.06e-06 | (1) | 1.77e-06 | (2) | 0.0036845
Molybdenum Trioxide | 1313-27-5 | 3.11e-06 | (1) | 3.11e-05 | (2) | 0.023999
Nickel | 7440-02-0 | 2.8e-06 | (1) | 1.32e-05 | (2) | 0.014072
Phosphorus and compounds | 7723-14-0 | 0.00031 | (1) | 0.00545 | (2) | 3.5885
Selenium | 7782-49-2 | 1.62e-06 | (1) | 3.25e-06 | (2) | 0.0059084
Silver and compounds | 7440-22-4 | 9.85e-07 | (1) | 0.000937 | (2) | 0.47959
Thallium and compounds | 7440-28-0 | 1.85e-06 | (1) | 1.85e-05 | (2) | 0.014276
Vanadium (fume or dust) | 7440-62-2 | 5.94e-07 | (1) | 5.94e-06 | (2) | 0.0045837
Zinc | 7440-66-6 | 0.00013 | (1) | 0.00129 | (2) | 0.99807
Notes and References:
(1) - NCASI TB 1013 Table 4.3 (mean values) for those boilers that were controlled by an “ESP/Fabric Filter” with the exception of thallium where the only data available was for a boiler with a scrubber.
(2) - NCASI TB 1013 Table 4.3 (mean values) for those boilers that were controlled by a "Mechanical Collector" only with the exception of molydenum trioxide, thallium and compounds and vanadium. For these pollutants, the steady state emission factors were use and it was assumed the ESP provided a control efficiency of 90%.

## Startup_Conditions
Attachment A
Table A-2
Seneca Sustainable Energy, LLC - 206470
SSE Boiler Startups - Heat Input Data
Fire in Fuel Cell |  | Started ESP |  | Duration of Startup | Fuel Used During Startup | Average of Last 3 HHV Tests | Heat Input During Startup | Heat Input Rate at ESP Start
date | time | date | time | hours | lb | btu/lb | MM Btu | MM Btu/hr
2015-05-16 | 6:10 | 2015-05-16 | 15:45 | 9.5 | 62455.8 | 5074 | 316.9007 | 66.7159
2015-07-26 | 13:10 | 2015-07-26 | 18:10 | 5 | 31726.6 | 5074 | 160.9808 | 64.3923
2015-08-29 | 17:30 | 2015-08-29 | 22:30 | 5 | 40452.9 | 5074 | 205.258 | 82.1032
2015-10-11 | 16:00 | 2015-10-11 | 20:00 | 4 | 54415.2 | 5107.6667 | 277.9347 | 138.9674
2015-12-13 | 13:00 | 2015-12-13 | 19:00 | 6 | 39227 | 5108 | 200.3715 | 66.7905
2016-05-14 | 4:30 | 2016-05-14 | 13:10 | 8.5 | 82651.2 | 5108 | 422.1823 | 99.337
2017-05-13 | 5:20 | 2017-05-13 | 14:30 | 9 | 79034 | 5195.3333 | 410.608 | 91.2462
2017-05-14 | 14:10 | 2017-05-14 | 19:35 | 5.5 | 49251.9 | 5195.3333 | 255.88 | 93.0473
2017-05-28 | 21:10 | 2017-05-29 | 6:20 | 9.25 | 98171 | 5195.3333 | 510.0311 | 110.277
2018-05-12 | 4:55 | 2018-05-12 | 12:46 | 8 | 63536 | 4953.6667 | 314.7362 | 78.684
2018-06-26 | 18:10 | 2018-06-26 | 22:10 | 4 | 26532.3 | 4953.6667 | 131.4322 | 65.7161
2018-12-12 | 7:30 | 2018-12-12 | 13:30 | 6 | 35279.4 | 4771 | 168.318 | 56.106
2019-05-10 | 19:00 | 2019-05-10 | 24:00 | 5 | 44463 | 4771 | 212.133 | 84.8532
2019-05-17 | 4:55 | 2019-05-17 | 11:30 | 6.5 | 61043.2 | 4771 | 291.2371 | 89.6114
|  |  | Averages | 6.5179 | 54874.25 | 5025.1429 | 277.0003 | 84.8463